## Info
Simulation results:
Sheet 'Optimal_results' contains optimal results of the optimization. However, the nominal values of the heat exchangers heat flow Q_n [W] do not correspond with heat exchangers offered in market. Sheet 'Particular_results' contains all feasible permutations of heat exchangers sets. Sheet 'Selected_results' shows some results that were selected as interesting.
Displayed values:
Q [W] | heat exchanger heat flow under actual conditions
Q_n [W] | nominal heat exchanger heat flow under catalogue conditions (depicted in setup .xlsm sheet)
m_dot [kg/h] | mass flow through heat exchanger
Twi [°C] | heat exchanger Inlet water temperature
Two [°C] | heat exchanger outlet water temperature | nominal heat flows
return water temperature

## Optimal_results
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C]
999.7258 | 1758.2601 | 490.321 | 60 | 58.2456
2002.1347 | 3818.62 | 490.2914 | 58.2456 | 54.7366
2290.4341 | 5000 | 490.2481 | 54.7368 | 50.3502
799.7951 | 1956.6483 | 421.4901 | 50.3509 | 48.7182
798.1678 | 2139.8917 | 224.4938 | 48.9474 | 45.8819
1196.4647 | 3343.01 | 490.3197 | 47.5439 | 45.4386
1197.6621 | 3710.441 | 490.3222 | 45.4386 | 43.3333
1384.2243 | 5000 | 490.2481 | 43.3333 | 39.9995
40

## Selected_results
Fobj | 3.348
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
1000.9839 | 1764 | 455.5251 | 60 | 58.1116 | PLAN_LINE_1000x700_Typ_21
1999.0941 | 3835 | 321.0911 | 59.0321 | 53.674 | VKM8_1100x700_Typ_20
2501.2062 | 4880 | 811.7465 | 57.0962 | 54.4469 | VKM8_1400x700_Typ_20
799.9978 | 2066 | 57.9346 | 54.6763 | 42.7979 | VKM8_1100x700_Typ_10
800.0149 | 2117 | 59.8946 | 53.902 | 42.4123 | PLAN_LINE_1200x700_Typ_21
1200.3211 | 3375 | 83.3426 | 53.1276 | 40.7419 | PLAN22_LINE33_1000x700_Typ_33
1199.9889 | 3713 | 76.0236 | 51.9661 | 38.388 | PLAN22_LINE33_1100x700_Typ_33
1899.9688 | 5401 | 185.9928 | 50.8046 | 42.0171 | PLAN22_LINE33_1600x700_Typ_33
48.9655

## Particular_results
Fobj | 3.2424 |  | m_dot_p [kg/h] | 980.6452
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
1001.7487 | 1764 | 468.1906 | 60 | 58.1627 | PLAN_LINE_1000x700_Typ_21
2000.3784 | 3835 | 313.2749 | 59.1228 | 53.631 | VKM8_1100x700_Typ_20
2499.9171 | 5401 | 246.1655 | 57.3684 | 48.6323 | PLAN22_LINE33_1600x700_Typ_33
799.9577 | 2066 | 54.0593 | 55.1754 | 42.4455 | VKM8_1100x700_Typ_10
799.8962 | 2190 | 50.2339 | 54.4737 | 40.7743 | PLAN_LINE_1600x700_Typ_11
1199.862 | 3375 | 76.6161 | 53.7719 | 40.2988 | PLAN22_LINE33_1000x700_Typ_33
1200.0114 | 3528 | 78.1586 | 52.7193 | 39.5121 | PLAN_LINE_2000x700_Typ_21
1899.9486 | 5401 | 158.8711 | 51.6667 | 41.379 | PLAN22_LINE33_1600x700_Typ_33
50
Fobj | 1.5416 |  | m_dot_p [kg/h] | 1961.2903
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
999.4959 | 1764 | 432.7666 | 60 | 58.0123 | PLAN_LINE_1000x700_Typ_21
1999.9514 | 3835 | 271.8076 | 59.5614 | 53.2318 | VKM8_1100x700_Typ_20
2498.8969 | 5401 | 193.5897 | 58.6842 | 47.5755 | PLAN22_LINE33_1600x700_Typ_33
800.0282 | 2066 | 41.1608 | 57.5877 | 40.8686 | VKM8_1100x700_Typ_10
799.966 | 2190 | 37.8944 | 57.2368 | 39.0766 | PLAN_LINE_1600x700_Typ_11
1199.8225 | 3375 | 55.8677 | 56.886 | 38.4091 | PLAN22_LINE33_1000x700_Typ_33
1199.9221 | 3528 | 54.3316 | 56.3596 | 37.3604 | PLAN_LINE_2000x700_Typ_21
1899.8304 | 4880 | 119.9019 | 55.8333 | 42.2021 | VKM8_1400x700_Typ_20
55
Fobj | 2.0144 |  | m_dot_p [kg/h] | 980.6452
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
1001.3422 | 1764 | 461.3711 | 60 | 58.1355 | PLAN_LINE_1000x700_Typ_21
1999.7315 | 3835 | 312.1906 | 59.1228 | 53.612 | VKM8_1100x700_Typ_20
2500.3124 | 5401 | 246.3879 | 57.3684 | 48.6402 | PLAN22_LINE33_1600x700_Typ_33
799.9807 | 1948 | 66.4997 | 55.1754 | 44.8269 | VKM8_800x700_Typ_11
800.0024 | 2190 | 50.251 | 54.4737 | 40.779 | PLAN_LINE_1600x700_Typ_11
1200.1999 | 3283 | 82.6175 | 53.7719 | 41.2775 | PLAN22_LINE33_1400x700_Typ_22
1199.9562 | 3713 | 69.7748 | 52.7193 | 37.9252 | PLAN22_LINE33_1100x700_Typ_33
1900.033 | 4880 | 258.3616 | 51.6667 | 45.3406 | VKM8_1400x700_Typ_20
50
Fobj | 3.2943 |  | m_dot_p [kg/h] | 972.9839
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
1001.3247 | 1764 | 461.0833 | 60 | 58.1344 | PLAN_LINE_1000x700_Typ_21
2000.1019 | 3835 | 313.5546 | 59.1159 | 53.629 | VKM8_1100x700_Typ_20
2501.2125 | 4880 | 685.5711 | 57.3477 | 54.2108 | VKM8_1400x700_Typ_20
799.8739 | 2066 | 54.3167 | 55.1374 | 42.4678 | VKM8_1100x700_Typ_10
800.081 | 2190 | 50.5302 | 54.4302 | 40.8112 | PLAN_LINE_1600x700_Typ_11
1199.927 | 3283 | 83.1126 | 53.7229 | 41.3029 | PLAN22_LINE33_1400x700_Typ_22
1199.8778 | 3528 | 78.7007 | 52.662 | 39.5457 | PLAN_LINE_2000x700_Typ_21
1899.8732 | 5401 | 160.6147 | 51.601 | 41.4251 | PLAN22_LINE33_1600x700_Typ_33
49.9213
Fobj | 3.348 |  | m_dot_p [kg/h] | 888.7097
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
1000.9839 | 1764 | 455.5251 | 60 | 58.1116 | PLAN_LINE_1000x700_Typ_21
1999.0941 | 3835 | 321.0911 | 59.0321 | 53.674 | VKM8_1100x700_Typ_20
2501.2062 | 4880 | 811.7465 | 57.0962 | 54.4469 | VKM8_1400x700_Typ_20
799.9978 | 2066 | 57.9346 | 54.6763 | 42.7979 | VKM8_1100x700_Typ_10
800.0149 | 2117 | 59.8946 | 53.902 | 42.4123 | PLAN_LINE_1200x700_Typ_21
1200.3211 | 3375 | 83.3426 | 53.1276 | 40.7419 | PLAN22_LINE33_1000x700_Typ_33
1199.9889 | 3713 | 76.0236 | 51.9661 | 38.388 | PLAN22_LINE33_1100x700_Typ_33
1899.9688 | 5401 | 185.9928 | 50.8046 | 42.0171 | PLAN22_LINE33_1600x700_Typ_33
48.9655
Fobj | 2.1909 |  | m_dot_p [kg/h] | 934.6774
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
1001.1862 | 1764 | 458.8075 | 60 | 58.1251 | PLAN_LINE_1000x700_Typ_21
2000.4151 | 3835 | 318.0608 | 59.0797 | 53.6705 | VKM8_1100x700_Typ_20
2500.7617 | 4880 | 732.1964 | 57.239 | 54.3019 | VKM8_1400x700_Typ_20
799.9991 | 2066 | 55.8349 | 54.9382 | 42.613 | VKM8_1100x700_Typ_10
799.9821 | 2117 | 57.3314 | 54.2019 | 42.1985 | PLAN_LINE_1200x700_Typ_21
1199.9989 | 3375 | 79.6473 | 53.4656 | 40.5053 | PLAN22_LINE33_1000x700_Typ_33
1199.8861 | 3528 | 81.8092 | 52.3612 | 39.7434 | PLAN_LINE_2000x700_Typ_21
1899.8654 | 4880 | 293.2109 | 51.2568 | 45.6827 | VKM8_1400x700_Typ_20
49.5082
Fobj | 3.2393 |  | m_dot_p [kg/h] | 950
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
1001.2737 | 1764 | 460.2425 | 60 | 58.131 | PLAN_LINE_1000x700_Typ_21
2000.8478 | 3835 | 317.1636 | 59.0945 | 53.6701 | VKM8_1100x700_Typ_20
2500.8849 | 4880 | 711.9921 | 57.2835 | 54.2631 | VKM8_1400x700_Typ_20
800.1232 | 1948 | 68.3578 | 55.0198 | 44.9526 | VKM8_800x700_Typ_11
800.0516 | 2117 | 56.5969 | 54.2954 | 42.1362 | PLAN_LINE_1200x700_Typ_21
1199.883 | 3283 | 84.8548 | 53.571 | 41.406 | PLAN22_LINE33_1400x700_Typ_22
1200.15 | 3713 | 71.6225 | 52.4844 | 38.072 | PLAN22_LINE33_1100x700_Typ_33
1900.2472 | 4880 | 280.5179 | 51.3978 | 45.5715 | VKM8_1400x700_Typ_20
49.6774
Fobj | 2.1475 |  | m_dot_p [kg/h] | 1961.2903
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
1001.4532 | 1764 | 463.2132 | 60 | 58.1429 | PLAN_LINE_1000x700_Typ_21
1999.8305 | 3757 | 336.6006 | 59.5614 | 54.4502 | VKM8_2000x700_Typ_10
2499.9278 | 5401 | 193.9381 | 58.6842 | 47.5954 | PLAN22_LINE33_1600x700_Typ_33
799.9973 | 2066 | 41.1573 | 57.5877 | 40.8672 | VKM8_1100x700_Typ_10
799.9983 | 2190 | 37.8972 | 57.2368 | 39.0779 | PLAN_LINE_1600x700_Typ_11
1199.9691 | 3375 | 55.8793 | 56.886 | 38.413 | PLAN22_LINE33_1000x700_Typ_33
1200.0023 | 3528 | 54.3371 | 56.3596 | 37.3624 | PLAN_LINE_2000x700_Typ_21
1900.0298 | 4880 | 119.9371 | 55.8333 | 42.2061 | VKM8_1400x700_Typ_20
55
Fobj | 0.28197 |  | m_dot_p [kg/h] | 1470.9677
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
1000.3145 | 1764 | 444.9953 | 60 | 58.0669 | PLAN_LINE_1000x700_Typ_21
1999.7056 | 3757 | 355.6812 | 59.4152 | 54.5782 | VKM8_2000x700_Typ_10
2499.8461 | 5401 | 208.5352 | 58.2456 | 47.933 | PLAN22_LINE33_1600x700_Typ_33
800.1299 | 2066 | 44.676 | 56.7836 | 41.38 | VKM8_1100x700_Typ_10
799.9671 | 2117 | 44.3193 | 56.3158 | 40.7882 | PLAN_LINE_1200x700_Typ_21
1200.1776 | 3375 | 61.3258 | 55.848 | 39.0156 | PLAN22_LINE33_1000x700_Typ_33
1200.076 | 3528 | 60.3297 | 55.1462 | 38.0359 | PLAN_LINE_2000x700_Typ_21
1899.868 | 4880 | 145.0442 | 54.4444 | 43.1761 | VKM8_1400x700_Typ_20
53.3333
Fobj | 3.2563 |  | m_dot_p [kg/h] | 2451.6129
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
1001.5979 | 1764 | 465.6365 | 60 | 58.1526 | PLAN_LINE_1000x700_Typ_21
1999.7343 | 3757 | 325.8068 | 59.6491 | 54.3686 | VKM8_2000x700_Typ_10
2499.7418 | 5401 | 186.0967 | 58.9474 | 47.3913 | PLAN22_LINE33_1600x700_Typ_33
799.9317 | 1948 | 45.0034 | 58.0702 | 42.7786 | VKM8_800x700_Typ_11
800.2281 | 2117 | 38.4653 | 57.7895 | 39.8987 | PLAN_LINE_1200x700_Typ_21
1200.0516 | 3375 | 53.1065 | 57.5088 | 38.0713 | PLAN22_LINE33_1000x700_Typ_33
1199.2887 | 3528 | 51.29 | 57.0877 | 36.9618 | PLAN_LINE_2000x700_Typ_21
1900.0245 | 4880 | 108.8581 | 56.6667 | 41.6525 | VKM8_1400x700_Typ_20
56
Fobj | 2.7093 |  | m_dot_p [kg/h] | 980.6452
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
1001.6153 | 1764 | 465.9299 | 60 | 58.1538 | PLAN_LINE_1000x700_Typ_21
2000.213 | 3757 | 403.5487 | 59.1228 | 54.8596 | VKM8_2000x700_Typ_10
2499.908 | 5401 | 246.1604 | 57.3684 | 48.6321 | PLAN22_LINE33_1600x700_Typ_33
800.0388 | 1948 | 66.5196 | 55.1754 | 44.83 | VKM8_800x700_Typ_11
800.0385 | 2117 | 55.2209 | 54.4737 | 42.0115 | PLAN_LINE_1200x700_Typ_21
1200.0513 | 3283 | 82.5881 | 53.7719 | 41.2731 | PLAN22_LINE33_1400x700_Typ_22
1200.0298 | 3528 | 78.1616 | 52.7193 | 39.5126 | PLAN_LINE_2000x700_Typ_21
1899.8003 | 4880 | 258.1488 | 51.6667 | 45.3354 | VKM8_1400x700_Typ_20
50
Fobj | 5.5637 |  | m_dot_p [kg/h] | 2451.6129
Q [W] | Q_n [W] | m_dot [kg/h] | Twi [°C] | Two [°C] | Type
999.213 | 1764 | 428.6961 | 60 | 57.9934 | PLAN_LINE_1000x700_Typ_21
2000.1502 | 3757 | 326.5837 | 59.6491 | 54.3812 | VKM8_2000x700_Typ_10
2497.7958 | 4880 | 343.4847 | 58.9474 | 52.6864 | VKM8_1400x700_Typ_20
799.984 | 2066 | 39.3273 | 58.0702 | 40.5716 | VKM8_1100x700_Typ_10
799.7823 | 2190 | 36.1554 | 57.7895 | 38.7558 | PLAN_LINE_1600x700_Typ_11
1199.988 | 3283 | 55.5973 | 57.5088 | 38.9421 | PLAN22_LINE33_1400x700_Typ_22
1200.1038 | 3713 | 48.0189 | 57.0877 | 35.5908 | PLAN22_LINE33_1100x700_Typ_33
1900.0668 | 4880 | 108.8641 | 56.6667 | 41.6534 | VKM8_1400x700_Typ_20
56